## Inspections
Installation | How often | Who | Rule | Usually applies to | Do you have it? | Last done | Next due | Report or certificate
Fire protection (RIPCI) | 3 and 6 months; 1 and 5 years; inspection every 10 years unless exempt | Owner (3 and 6 months), maintenance company (1 and 5 years), inspection body (10) | RD 513/2017 (RIPCI), Arts. 21 and 22 and Annex II | Restaurants and bars, Gyms, Hotels, Residents' associations, Shops and franchises, Offices, Schools, Industrial units
Self-protection plan | Drill at least once a year; plan reviewed at least every 5 years | The owner of the activity; drafted and signed by a qualified technician | Basic Self-Protection Directive (Orden INT/1068/2026), Annexes I and II | Gyms, Hotels, Shops and franchises, Offices, Schools, Industrial units
Low-voltage inspection | Every 5 years; every 10 for residential common areas over 100 kW | An accredited inspection body (OCA) for low voltage | REBT (Royal Decree 842/2002), ITC-BT-05 | Restaurants and bars, Gyms, Hotels, Residents' associations, Shops and franchises, Offices, Schools, Industrial units
Thermal installations (RITE) | Maintenance per table 3.1; inspection every 4 years above 70 kW | Maintenance company; inspection by an independent accredited expert | RITE (Royal Decree 1027/2007, amended by RD 178/2021) | Restaurants and bars, Gyms, Hotels, Residents' associations, Shops and franchises, Offices, Schools, Industrial units
Legionella | Hot water: daily temperature; yearly disinfection; quarterly Legionella test | Holder; treatment by qualified staff or a ROESB-registered firm | RD 487/2022, annexes IV and V | Restaurants and bars, Gyms, Hotels, Offices, Schools, Industrial units
Lift inspection | Monthly maintenance; inspection every 2, 4 or 6 years by building type | Lift maintenance company and inspection body (OCA) | ITC AEM 1 (RD 355/2024), Arts. 5 and 11 | Hotels, Residents' associations, Offices, Schools
Swimming pools | Public use: daily check before opening and monthly lab analysis | Holder, with trained staff and a laboratory | RD 742/2013, Arts. 3 and 11 and annex III | Gyms, Hotels, Residents' associations
HACCP (APPCC) | Permanent; reviewed when a product or a process changes | The business itself, with a named person; no external certificate | Regulation (EC) 852/2004, Art. 5 and annex II; RD 1021/2022, Art. 20 | Restaurants and bars, Hotels, Schools
Defibrillator (AED) | Maintenance per the manufacturer; report each use (72 h in several regions) | The holder of the premises: notification, maintenance and trained staff | RD 365/2009 plus each region's decree (Madrid, Catalonia, Andalusia…) | Gyms, Hotels, Shops and franchises

## How to use it
In «Do you have it?», mark No for what you do not have (pool, lift, gas…) and filter by Yes.
«How often» and «Who» are those of the Spanish national rule; the exact condition (power, capacity, size) is on each installation's page at bedel.es/normativa.
Fill in «Last done» with the date of the latest report or certificate, not from memory, and work out «Next due».
Once a month, sort by «Next due»: whatever falls in the next three months, call now, because contractors and inspection bodies have diaries too.
Keep the paperwork where «Report or certificate» says: at an inspection it is shown, not told.
Spanish national rules read in the BOE on 19 Oct 2026. Your region and your council may require more.
Template from bedel.es · https://www.bedel.es/en/plantillas/calendario-inspecciones-obligatorias