## Preventive plan
Installation or equipment | Task | How often | Who | Compulsory or recommended | Rule | Last done | Next due | Done by and notes
Electrical installation | Periodic inspection by an inspection body | Every 5 years | Inspection body (OCA) | Compulsory | REBT, ITC-BT-05 (4.2) and ITC-BT-28
Emergency lighting | Cut the power and check it comes on | Every month | Own staff | Recommended | Having it: ITC-BT-28 (2.3); the test, a guide
Extinguishers and fire equipment | In place, accessible, sealed and with pressure in the operating zone | Every 3 months | The holder | Compulsory | RD 513/2017, annex II
Extinguishers and fire equipment | Servicing with a written report | Every year | Maintenance company | Compulsory | RD 513/2017, Art. 21 and annex II
Extinguishers | Level C test | Every 5 years | Maintenance company | Compulsory | RD 513/2017, annex II
Hot water (Legionella) | Check the temperature | Daily | Own staff | Compulsory | RD 487/2022, annex IV
Hot water (Legionella) | Cleaning and disinfection | Every year | Own staff or a company | Compulsory | RD 487/2022, annex IV
Terrace misting units (if any) | Check and clean the nozzles | Every month | Own staff | Compulsory | RD 487/2022, annex V
Terrace misting units (if any) | Legionella test | Every 6 months | Laboratory | Compulsory | RD 487/2022, annex V
Heating and cooling (up to 70 kW) | Servicing with a log | Every 1 or 2 years, per table 3.1 | Maintenance company | Compulsory | RD 1027/2007 (RITE), IT 3.3
Kitchen gas (if any) | Periodic check of the installation | Every 5 years | Qualified gas installer or distributor | Compulsory | RD 919/2006, Art. 7; ITC-ICG 07
Cold rooms and fridges | Record the temperature | Set by your HACCP | Own staff | Compulsory | Regulation (EC) 852/2004, Art. 5
Pest control | Check as per your procedure | Set by your procedure | Own staff; professional biocides, qualified staff | Compulsory | Regulation (EC) 852/2004, annex II; RD 830/2010
Extractor hood: filters | Remove and degrease the filters | Every week, depending on use | Own staff | Recommended | None of those cited: a guide
Extractor hood: ductwork | Duct cleaning | Depending on use and manufacturer | Specialist company | Recommended | None of those cited: a guide
Fryers | Change the oil and clean the vat | Depending on use | Own staff | Recommended | None of those cited: a guide
Cold rooms and fridges | Clean the condenser, check seals and drain | As per manufacturer | Own staff or refrigeration firm | Recommended | None of those cited: a guide
Dishwasher | Descale, clean arms and filters | As per manufacturer | Own staff | Recommended | None of those cited: a guide

## How to use it
Delete the rows for what you do not have (gas, misting units) and add your own equipment.
Fill in «Last done» with the date of the latest report or certificate, and «Next due» by adding the frequency.
Every Monday, sort by «Next due»: whatever falls this month, call the right company now.
«Compulsory» tasks carry their rule: keep the report or certificate for the inspection.
«Recommended» tasks are not required by any of the rules cited: their frequency is a guide; the manufacturer and use decide.
This plan is for what is done before something fails. Day-to-day faults go in a separate log.
Spanish rules read in the BOE on 19 Oct 2026. Your region and your council may require more.
Template from bedel.es · https://www.bedel.es/en/plantillas/plan-mantenimiento-preventivo-restaurante